## Safety Comparison
EMF Analysis Table
Current (A) | Height (m) | Electric Field (kV/m) | ICNIRP Limit (kV/m) | MAGNETIC FIELD (µT) | ICNIRP Limit (µT)
1000 | 1 | 0.05 | 5 | 2.72 | 100
1000 | 15 | 0.61 | 5 | 6 | 100
1000 | 30 | 3.04 | 5 | 23.56 | 100
1000 | 50 | 5.99 | 5 | 45.44 | 100
750 | 1 | 0.05 | 5 | 2.04 | 100
750 | 15 | 0.61 | 5 | 4.5 | 100
750 | 30 | 3.04 | 5 | 17.67 | 100
750 | 50 | 5.99 | 5 | 34.08 | 100
500 | 1 | 0.05 | 5 | 1.36 | 100
500 | 15 | 0.61 | 5 | 3 | 100
500 | 30 | 3.04 | 5 | 11.78 | 100
500 | 50 | 5.99 | 5 | 22.72 | 100
s

## Horizontal Profile
Distance from Tower Center (m) | Electric Field (kV/m) | Magnetic Field (µT) | E-Field % of Limit | B-Field % of Limit
0 | 0.054 | 2.72 | 1.1% | 2.7%
10 | 0.446 | 1.991 | 8.9% | 2.0%
20 | 0.29 | 0.877 | 5.8% | 0.9%
30 | 0.163 | 0.458 | 3.3% | 0.5%
40 | 0.099 | 0.271 | 2.0% | 0.3%
50 | 0.064 | 0.179 | 1.3% | 0.2%

## Vertical Profile
Height Above Ground (m) | Electric Field (kV/m) | Magnetic Field (µT) | Description
0 | 0.044 | 2.608 | Ground level
1 | 0.054 | 2.72 | Human height (standing)
2 | 0.066 | 2.832 | Head height (tall person)
5 | 0.118 | 3.231 | Low elevation
10 | 0.244 | 4.043 | Mid elevation
15 | 0.423 | 5.264 | Mid-high elevation
20 | 0.675 | 7.146 | High elevation
25 | 1.015 | 10.155 | Near lower conductors
30 | 1.474 | 15.262 | Between conductor levels

## Specifications
Parameter | Value | Notes
System Voltage | 400 kV | Line-to-line voltage
Phase Voltage | 230.9 kV | Line-to-neutral voltage
Operating Current | 1000 A | Per phase
Frequency | 50 Hz | European standard
Configuration | Double Circuit | Vertical configuration
Number of Conductors | 6 (3 per circuit) | 3-phase system
Tower Height | 50 m | Lattice steel tower
Upper Conductor Height | 45 m | Circuit 1 elevation
Lower Conductor Height | 40 m | Circuit 2 elevation
Phase Spacing | 8 m | Horizontal separation
Conductor Radius | 0.015 m (15 mm) | Equivalent radius
Tower Base Width | 12 m | Ground-level dimension
Tower Top Width | 3 m | Top dimension

## Methodology
Field Type | Aspect | Details
Electric Field | Method | Charge Simulation Method (CSM) with Method of Images
Electric Field | Key Formula | E = q / (2πε₀r) where q = line charge density
Electric Field | Boundary Condition | Ground plane at V = 0, image charges below ground
Magnetic Field | Method | Biot-Savart Law for infinite straight conductors
Magnetic Field | Key Formula | B = (μ₀I) / (2πr) where I = conductor current
Magnetic Field | Approximation | 2D cross-section, perpendicular to line direction